## Sky heat pump
WESTON CLIMATE
WMD Company Sp.Z.O.O. ul. KIELECKA 4/5 31-526 KRAKÓW MAŁOPOLSKIE +48 451 115 524 sales@westonclimate.pl ¦ www.westonclimate.pl
Heat Pump (Inverter Top Blow Design Heating&Cooling&DHW)
Standard Configuration | Heat pump and indoor hydraulic box
Picture
Model | WESTON-JN-MN-TOP-R290-5KW-1F | WESTON-JN-MN-TOP-R290-7KW-1F | WESTON-JN-MN-TOP-R290-9KW-230V-1F | WESTON-JN-MN-TOP-R290-12KW-230V-1F | WESTON-JN-MN-TOP-R290-15KW-230V-1F | WESTON-JN-MN-TOP-R290-15KW-380V-3F | WESTON-JN-MN-TOP-R290-20KW-380V-3F
Heating Capacity Range (kW) | 5 | 7 | 9 | 12 | 15 | 15 | 20
Price | 1513.26 | 1771.04 | 1830.47 | 2133.92 | 2613.45 | 2676.14 | 3141.43
Standard Configuration set price | 1513.26 | 1771.04 | 1830.47 | 2133.92 | 2613.45 | 2676.14 | 3141.43
Heating Capacity Range (kW) | 2-5 | 2.4-7 | 2.8-10 | 3.2-12 | 4.9-15 | 4.9-15 | 6.6-20
Heating (A7/6℃,W30/35℃)
Heating Capacity (kW) | 5 | 7 | 9 | 12 | 15 | 15 | 20
Power Input (kW) | 1.068 | 1.515 | 1.935 | 2.553 | 3.19 | 3.19 | 4.2553
COP | 4.6816 | 4.6205 | 4.6512 | 4.7004 | 4.7022 | 4.7022 | 4.7
Heating (A7/6℃,W40/45℃)
Heating Capacity (kW) | 5 | 7 | 9 | 12 | 15 | 15 | 20
Power Input (kW) | 1.37 | 1.939 | 2.466 | 3.288 | 4.155 | 4.155 | 5.5402
COP | 3.6496 | 3.6101 | 3.6496 | 3.6496 | 3.6101 | 3.6101 | 3.61
Heating (A7/6℃,W47/55℃)
Heating Capacity (kW) | 5 | 7 | 8.5 | 11 | 14 | 14 | 19
Power Input (kW) | 1.613 | 2.258 | 2.787 | 3.548 | 4.59 | 4.59 | 6.4407
COP | 3.0998 | 3.1001 | 3.0499 | 3.1003 | 3.0501 | 3.0501 | 2.95
Cooling (A35/24℃,W23/18℃)
Cooling Capacity (kW) | 4.5 | 5.5 | 7 | 10 | 13 | 13 | 17
Power Input (kW) | 1.154 | 1.41 | 1.842 | 2.564 | 3.33 | 3.33 | 4.359
EER | 3.8995 | 3.9007 | 3.8002 | 3.9002 | 3.9039 | 3.9039 | 3.9
Cooling (A35/24℃,W12/7℃)
Cooling Capacity (kW) | 4.5 | 5.5 | 7 | 10 | 13 | 13 | 17
Power Input (kW) | 1.607 | 1.897 | 2.574 | 3.571 | 4.727 | 4.727 | 6.3433
EER | 2.8002 | 2.8993 | 2.7195 | 2.8003 | 2.7502 | 2.7502 | 2.68
General Information
Power Supply | 220V~240V/50Hz/60Hz |  |  |  |  | 380~415V/50Hz/60Hz
Refrigerant | R290
Operating Air Temp.(℃) | -25~43
Max.Outlet Water Temp(℃) | 75
Max Power Input (kW) | 3.68 | 4.14 | 4.83 | 5.29 | 7.36 | 7.36 | 9.56
Max Current (A) | 16 | 18 | 21 | 23 | 32 | 16 | 20
General Configuration
Controller | 5.0 inches Colorful LED Touchscreen
DTU (Data Transfer unit) and RS485 Modbus | Yes (WIFI Version), Remote control
WIFI | Yes
Compressor | HIGHLY (Rotary)
Fan Quantity | 1
Heat Exchanger | Danfoss Plate heat exchanger
EEV (Electronic expansion valve) | SANHUA
Built-in Circulating pump | SHIMGE (Inverter)
Water flow meter | SIKA (Original German-Made)
Deaerator | Anti oxidation corrosion and avoid refrigerant leakage
Casing Material | Galvanized Sheet
Water Pipe Connection (inch) | G1" (Male thread) | [5 empty] | G1 1/4' (Male thread)
Noise sound power Level dB(A) | 52 | 52 | 52 | 55 | 55 | 55 | 55
Noise sound pressure Level dB(A) @ 1m | 41 | 41 | 41 | 44 | 44 | 44 | 44
Water Flow (m³/h) | 1.03 | 1.38 | 1.72 | 2.06 | 2.58 | 2.58 | 3.44
Water Pressure Drop (kPa) | 10 | 15 | 20 | 25 | 30 | 30 | 35
Net Dimensions ( L/W/H ) mm | 700*685*908 | 700*685*908 | 700*685*908 | 1130*630*935 | 1130*630*935 | 1130*630*935 | 1300*710*935
Package Dimensions ( L/W/H ) mm | 791*757*1061 | 791*757*1061 | 791*757*1061 | 1220*730*1090 | 1220*730*1090 | 1220*730*1090 | 1390*770*1095
Net Weight KG | 74 | 75 | 90 | 118 | 138 | 138 | 195
Gross Weight KG | 88 | 90 | 110 | 141 | 163 | 163 | 245
Loading quantity 20GP/40GP,40HQ pcs Heat pump and indoor hydraulic box | 36/90/90 | 36/90/90 | 36/90/90 | 24/56/56 | 24/56/56 | 24/56/56 | 24/50/50

## Indoor Unit Configuration
Optional Indoor Unit Configuration
Product Name | Hydraulic Box
Picture
Model | NHB-02 | NHB3N-01
Power Supply | 220~240V/50Hz/60Hz | 380-415V/50Hz/60Hz
Expansion Tank | 5L | 5L
Electric Heating Heater | 3kW | 6kW
AC Contactor 1 (Main Board) (Both are 220-240V voltage connection) | 16A | 16A
AC Contactor 2 (DHW Electric Heater Terminal) | 63A | 25A
AC Contactor 3 (Heating Electric Heater Terminal) | 63A | 25A
AC Contactor 4 (Inner Electric Heater Terminal) | 16A | 25A
3-Way Valve | Yes | Yes
Automatic Air Release Valve | Yes | Yes
Communication Connecting Wire Length (Indoor unit & Outdoor unit) | 15m | 15m
Connecting Wire Length (Temp. Sensors) | 5m | 5m
Product Size (L/W/H) mm | 420*249*610 | 420*249*610
Package Dimensions (Wood Fiber Box, L/W/H ) | 480*312*700 | 480*312*700
Adapt model | JMU50HC JMU70HC JMU90HC JMU120HC JMU150HC | JMU150HC3N JMU200HC3N